## Sheet1
FORMAT I: Fatal and non-fatal accident report
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Number of Accidents during the month |  |  |  |  | Cumulative since starting of year |  | Cumulative since starting of year
Departmental |  | Outside |  |  | Departmental |  | Outside
FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
0 | 0 | 4 | 0 | 3 | 0 | 0 | 6 | 0 | 7
FH- Fatal Human
NFH- Non Fatal Human
FA- Fatal Animal
FORMAT II: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Sl. No. | Location of accident and details of victim | Date of occurrence | Type of accident | Cause of accident | Findings of CEI/EI /AEI | Remedies suggested by CEI/EI/AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such accidents | Amount paid as compensation
1 | Raju Enclave Near Vishwakarma Mandir. | 04.07.2019 at around 02:24 / 02:46 PM | Fatal | A complaint has been received on dated 04.07.2019 at around 02:34 / 02:46 PM (PCR Complaint) has been received through IOMS) vide entry No. 6026 / 6153 dated 04.07.2019 address Raju Enclave Near Vishwakarma Mandir. Sh. Rahul Telephone Operator on dated Deputed Sh. Krishan LM (Telephonically Message at 02:45 PM to attend this PCR complaint. Telephone operator also informed to Sh. Intezar Ali supervisor about this matter. Lineman attended the same and checked the complete network on PCC pole DWK E 551 (near house number RZ 27 / 11 plot number 8 Raju enclave old palam road). Our staff checked the all network on this pole where incident occurred. It has been found that there is no discrepancy found observed at site. Again a PCR message received in IOMS 6153 at 02:46 pm showing that a wire lying on ground on subjected Pole. Both complaints have been attended by Shri Krishan lineman but there was no wire found from site during visit by our staff. Our Staff asked nearby subjected site what happened ? nearby consumers stated that a child has been electrocuted. Safety Officer West 1 is requested to visit the subjected site jointly. | N.A. | N.A. | N.A. | N.A. | N.A.
2 | Near H.No E-175, Vishkarma Colony, Lal Kuan, New Delhi | 05.07.2019 at about 12:30 PM | Non-Fatal | A telephonic complaint was received from Lal Kuan near Bharat Gas Godown on 05.07.2019 at about 12:30 PM that a boy named Sanjay aged 8 yrs approximately got electric shock from some nearby cable. Sh. Sahil Lineman and Sh. Surjit Supervisor visited the site and found two incoming cables from pole are cut down and make a temporary arrangement on a wall intentionally for theft purposes by some local public. Also some building works are going on that sitewhere another meter cable also cut down and put U/G from the wall where theft arrangement found. There are no other U/G service line in that area. The boy was playing with his friend near the wall and somehow he touched the open part of the cable and got electric shock. Nearby public / family members taken him to hospital and he is now out of danger. | N.A. | N.A. | N.A. | N.A. | N.A.
3 | j-11 / 135, third floor, Rajouri Garden, New delhi 110027. | 05.07.2019 | Fatal | on dated 05.07.2019 at about 9:50 AM, a PCR Complaint received through online in IOMS vide complaint No 19070502179 regd. Current leakage in house. Immediately Lineman deputed at site who found / informed that an incident of electrocution has been occurred at J-11 / 135 third floor, Rajouri Garden due to current leakage in House electrical wiring. BSES disconnected the power supply of the premise for safety reasons (C.A.No 102889684 & Meter No 40481077) | N.A. | N.A. | N.A. | N.A. | N.A.
4 | Sub Station Bhim Colony, Delhi | 10.07.2019 at about 07:30 PM | Non-Fatal | The information gather from site reveals that a boy of 5 years old named Lucky was playing with his friends near Sub station Bhim Colony, when a ball with which they were playing fell inside the Sub station Bhim Colony. Master Lucky while trying to take out the ball reportedly came in contact with HT 11 kv Line inside Sub station at around 07:30 PM on dated 10.07.2019. In this process, he got an electric shock. The HT line got tripped from the RMU at Priyanka Camp. He was taken to Safdarjung for treatment and is presently under observation in the hospital. | N.A. | N.A. | N.A. | N.A. | N.A.
5 | Jonapur Village, Delhi. | 21.07.2019 | Fatal | The accident took place at connecting road from 7th Avenue RMB to Jonapur Village. There was heavy thunder strom and rain in the Aya Nagar region as per IMD. The BSES HT conductor was broken at 03:35 PM (approximately) and our 11KV O/G feeder NBCC from C DOT grid was tripped / disconnected from NBCC Bhatta Substation, so the reason of accident is not cleared. After accident victims namely Md. Salim and Sh. Hoshiyar Singh Rawat were taken by Delhi Police as per sources. The police has seized the broken conductor. The status quo is as it is from BSES point of view. No BSES employee was present at the time of accident. | N.A. | N.A. | N.A. | N.A. | N.A.
6 | Near Police Station Jaitpur. | 27.07.2019 at about 02:00 AM | Fatal | On 27.07.2019 at about 10:30 AM calls received from public representatives that an electrical accident had occurred on 27.07.2019 at about 02:00 AM when a group of kavadiya boys were moving under 11 kv road crossing conductors of said feeder. The height of the truck along with DJ installations and structures mounted therein was more than specified RTO limits. The probable cause of accident is unknown in which one person is reported to be electrocuted and fell down from the truck - he died. During the night we received individual category NCC at about 02:10 AM and area was checked and when lineman found no fault - the area was energized. Accident situation remained unknown at night. There is regular daily movement of buses and high trucks on this road, but they do not touch the conductors. | N.A. | N.A. | N.A. | N.A. | N.A.
7 | Pole No. BSES SVR V-124 & premise house no. F-33 / 3, GF, Block-F, Gali No. 3, Molarband Extn, Badarpur, New Delhi | 28.07.2019 at about 12:25 PM | Non-Fatal | On dated 28.07.2019 at about 12:25 PM complaint registered for electricity off in the area. Sh. Laki, Lineman visited the site found tripping from sub station no. 8 MB Extn. Also DD fuse blown off at F Block HVDS DP supply restored and at that place found electrical accident occured at Gali No. 3 F Block MB Extn. due to which tripping occured from these places. As per information gathered at site Smt. Punita Kumari victim fell down sariya from roof which was got unballanced and got touched upon the HVDS DD fuse and tripping occured. | N.A. | N.A. | N.A. | N.A. | N.A.
FORMAT III: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | Within Specified Time | Beyond specified time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9
Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  |  | - | 132759 | 132759 | 132759 | 0 | 132759 | 0
Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  |  |  | 23982 | 23982 | 23902 | 80 | 23982 | 0
Continuous power supply failure requiring replacement of distribution transformer. |  |  |  | 10 | 10 | 10 | 0 | 10 | 0
Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) |  |  |  | 50379 | 50379 | 50379 | 0 | 50379 | 0
Continuous Schduled Power Outage |  |  |  | 783 | 783 | 783 | 0 | 783 | 0
Replacement of Burnt Meter or Stolen Meter |  |  | 21 | 4654 | 4675 | 4155 | 491 | 4646 | 29
FORMAT IV: Quality of Power Supply
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | Within Specified Time | Beyond specified time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Local Problem |  | 4 hours | 0 | 5338 | 5338 | 5338 | 0 | 5338 | 0
Tap setting of transformer
Repair of Distribution Line/transformer/ capacitor
Installation and Up gradation of High Tension/ Low Tension System
FORMAT V: Complaint about meters
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaint lodged for accuracy test of meter-Fast |  | Within fifteen days | 1200 | 3980 | 5180 | 2526 | 325 | 2851 | 2329
Complaint lodged for accuracy test of meter-Slow |  | Within fifteen days | 0 | 0 | 0 | 0 | 0 | 0 | 0
Complaint lodged for defective / stuck meter |  | Within fifteen days | 583 | 2460 | 3043 | 1558 | 1067 | 2625 | 418
Complaint lodged for burnt meter |  | Restoration of supply with 3hrs and meter to be replaced within 3days. | 962 | 4958 | 5920 | 3516 | 1701 | 5217 | 703
Complaint lodged for stolen meter |  |  | 5 | 54 | 59 | 41 | 9 | 50 | 9
FORMAT VI: New Connections / Additional Load, where power suppply can be provided from existing network
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
New Connection where no RoW or road Cutting permission is required |  | 7 days | 4676 | 18621 | 23297 | 11674 | 3996 | 15670 | 7627
New Connection where RoW or road Cutting permission is required |  | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connection where no RoW or road Cutting permission is required |  | 7 days | 209 | 223 | 432 | 176 | 27 | 203 | 229
New Connection where RoW or road Cutting permission is required |  | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT VII: Applications for New Connections / Additional Load, where power supply requires extension of distribution system.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
1. Electrified Areas (where extension of line upto five poles is required) |  | 15 days from receipt of payment
2. Electrified areas (where extension of lines or augmentation of Distribution Transformer capacity where peak load of transformer has reached 90% of its rated capacity. |  | Within 2 months from receipt of payment
3. Electrified areas (where new distribtion transformer is required) |  | Within 4 months from receipt of payment
4. Electrified Areas (where existing 11 KV network needs to be augmented) |  | 15 days
5. Electrified Areas (where existing 66/33 kV substation needs to be augmented) |  | 15 days
New Connections |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Load |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT VIII: Connection in un-electrified areas
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Un-Electrified Areas (Where connection from nearby existing network is possible) |  | Within 4 months from Commission's approval | 8 | 11 | 19 | 12 | 0 | 12 | 7
Un-Electrified Areas/ Green Field Projects (Where new network is to be laid or grid station needs to be established) |  | Within 12 months from Commission's approval | 0 | 1 | 1 | 1 | 0 | 1 | 0
FORMAT IX: Transfer of Consumer's connection and conversion of services.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Transfer of Name |  | Within two billing cycles of acceptance of application or clearing of dues whichever is later | 187 | 3805 | 3992 | 3762 | 77 | 3839 | 153
Load Reduction |  | Within ten days of acceptance of application, shall be effective from next billing cycle | 160 | 2551 | 2711 | 2495 | 26 | 2521 | 190
Change of Category |  | As per Regulation 17 (5) | 848 | 1304 | 2152 | 868 | 57 | 925 | 1227
Incase connection is denied after receipt of payment against demand note |  | - | 14 | 318 | 332 | 26 | 246 | 272 | 60
Connection energized through Loop |  | As per Regulation 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If notice towards downward if any is not sent |  | 31st May of Financial year | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT X: Complaints about consumer's bills, disconnection, reconnection of supply.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaints on billing |  | Only one bill in a Financial Year | 1331 | 1255 | 2586 | 1090 | 42 | 1132 | 1454
Final bill for vacation of premises / change of occupance. |  | 5 days | 49 | 128 | 177 | 130 | 2 | 132 | 45
Non payment of dues by the consumer |  | 15 days | 10 | 187 | 197 | 186 | 0 | 186 | 11
Request for reconnection |  | 24hrs | 80 | 1067 | 1147 | 740 | 300 | 1040 | 107
Consumer wanting disconnection |  | 5 days | 887 | 4927 | 5814 | 3051 | 1963 | 5014 | 800
FORMAT XI: Failure of Distribution Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
No. of Distribution transformers at the beginning of the month |  | No. of Distribution transformers added during the month |  | Total number of distribution transformers |  | Number of Distribution transformers failed |  | % Failure rate of distribution transformers
1 |  | 2 |  | 3=1+2 |  | 4 |  | 5=(4)*100/(3)%
7298 |  | 20 |  | 7318 |  | 6 |  | 8.199%
Note: | Only 3 phase transformers considered>=400 kVA
Only New transformers added in the system is considered against point no. 2
Only O&M failure considered
FORMAT XII: Failure of Power Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
No. of power transformers at the beginning of the month |  | No. of power transformers added during the month |  | Total number of power transformers |  | Number of power transformers failed |  | % Failure rate of power transformers
1 |  | 2 |  | 3=1+2 |  | 4 |  | 5=(4)*100/(3)%
255 |  | 1 |  | 256 |  | 0 |  | 0%
FORMAT XIII: Summary of Overall Standards of Performance.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Sl. No. | Service area |  | Overall Standards of Performance | Total Cases Received / Reported (A) |  | Complaints Attended (B) |  | Standard of Performance Achieved (C)
[6 empty] | Within Specified Time | Beyond specified time
1. Power Supply Failure
(i) | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  | 132759 |  | 132759 | 0 | 100%
(ii) | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  | 23982 |  | 23902 | 80 | 99.67%
(iii) | Continuous power supply failure requiring replacement of distribution transformer. | Continuous power supply failure requiring replacement of distribution transformer. |  | 10 |  | 10 | 0 | 100%
(iv) | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above |  | 50379 |  | 50379 | 0 | 100%
(v) | Continuous scheduled power outages | Continuous scheduled power outages |  | 783 |  | 783 | 0 | 100%
(vi) | Replacement of burnt meter | Replacement of burnt meter or stolen meter |  | 4675 |  | 4155 | 491 | 88.88%
Period of Scheduled Outage
2 | Maximum duration in a single stretch |  |  | 07H:12M
| Restoration of supply by 6:00 PM |  |  | ALL
3 | Faults in street light maintained by the licensee |  |  | 4735 |  | 4733 | 2 | 99.96%
Reliability Indices
4 | SAIFI |  |  | 0.49
| SAIDI |  |  | 0.28
| CAIDI |  |  | 0.57143
5 | Frequency variation |  |  | 0 |  | 0 | 0 | 0
6 | Voltage imbalance |  |  | 0 |  | 0 | 0 | 0
7 | Percentage billing mistakes |  |  | 0 |  | 0 | 0 | 0
* New method used for reliabilty index calculation*
FORMAT XIV: Compensation Details
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Sl. No. | Event |  | Compensation specified for violation of standard |  | Claimed |  | Payable/Paid
[5 empty] | No. of Cases | Amount Claimed | No. of cases in which compensation is payable | Amount of compensation payable in (Rs.) | Amount of compensation paid in (Rs.)
1 | Electricity connections
(i) | Electrified Areas | Electrified Areas | 1.5% of the demand charges deposited by consumer for each day of default.
(ii) | Augmentation Required | Augmentation Required | 1.5% of the demand charges deposited by consumer for each day of default | 1.5% of the demand charges deposited by consumer for each day of default
(iii) | Un-electrified Areas | Un-electrified Areas | 1% of the amount deposited by developer/applicants per day of default. | 1% of the amount deposited by developer/applicants per day of default.
(iv) | Connection denied after receipt of payment against demand note | Connection denied after receipt of payment against demand note | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment.
(v) | Connection energized through loop | Connection energized through loop | Rs. 500 per kW of sanctioned/ contract demand | Rs. 500 per kW of sanctioned/ contract demand
2 | Transfer of Name | Transfer of Name | Rs. 100 for each day of default. | Rs. 100 for each day of default.
3 | Load Reduction | Load Reduction | Rs. 100 for each day of default | Rs. 100 for each day of default
4 | Notice for downward revision of load | Notice for downward revision of load | Rs. 500 for each case | Rs. 500 for each case
5 | Change of category | Change of category | Rs. 100 for each day of default | Rs. 100 for each day of default
6 | Complaints in billing | Complaints in billing | 10% of excess amount billed | 10% of excess amount billed
7 | Replacement of meters | Replacement of meters | Rs.50 for each day of default | Rs.50 for each day of default
8 | Fault in street light maintained by the Licensee | Fault in street light maintained by the Licensee | Rs. 75 for each day of default | Rs. 75 for each day of default
9 | Voltage fluctuations and complainsts | Voltage fluctuations and complainsts
10 | Power Supply Failure | Power Supply Failure
11 | Total | Total
FORMAT XV: Unauthorized Use of Electricity
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
No. of Cases Booked |  | No. of Cases where UUE is established by the Licensee |  | No. of cases where appeal filed by the consumer before the Appellate Authority |  | No. of cases decided by the Appellate Authority in favor of the Licensee |  | No. of cases decided by the Appellate Authority in the favor of the consumer
747 |  | 743 |  | 0 |  | 3 |  | 0
FORMAT XVI: Theft of Electricity
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
No. of Cases Booked |  | No. of complaints filed by the Licensee in Police Station |  | No. of cases in which judgement delivered by the Special Court |  | No. of cases decided by the Special Court in favor of Licensee |  | No. of cases decided by the Special Court in favor of Consumer
1021 |  | 405 |  | 4 |  | 0 |  | 4

## FORMAT I
FORMAT I: Fatal and non-fatal accident report
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Number of Accidents during the month |  |  |  |  | Cumulative since starting of year |  | Cumulative since starting of year
Departmental |  | Outside |  |  | Departmental |  | Outside
FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
0 | 0 | 4 | 0 | 3 | 0 | 0 | 6 | 0 | 7
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FH- Fatal Human
NFH- Non Fatal Human
FA- Fatal Animal

## FORMAT II
FORMAT II: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Sl. No. | Location of accident and details of victim | Date of occurrence | Type of accident | Cause of accident | Findings of CEI/EI /AEI | Remedies suggested by CEI/EI/AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such accidents | Amount paid as compensation
1 | Raju Enclave Near Vishwakarma Mandir. | 04.07.2019 at around 02:24 / 02:46 PM | Fatal | A complaint has been received on dated 04.07.2019 at around 02:34 / 02:46 PM (PCR Complaint) has been received through IOMS) vide entry No. 6026 / 6153 dated 04.07.2019 address Raju Enclave Near Vishwakarma Mandir. Sh. Rahul Telephone Operator on dated Deputed Sh. Krishan LM (Telephonically Message at 02:45 PM to attend this PCR complaint. Telephone operator also informed to Sh. Intezar Ali supervisor about this matter. Lineman attended the same and checked the complete network on PCC pole DWK E 551 (near house number RZ 27 / 11 plot number 8 Raju enclave old palam road). Our staff checked the all network on this pole where incident occurred. It has been found that there is no discrepancy found observed at site. Again a PCR message received in IOMS 6153 at 02:46 pm showing that a wire lying on ground on subjected Pole. Both complaints have been attended by Shri Krishan lineman but there was no wire found from site during visit by our staff. Our Staff asked nearby subjected site what happened ? nearby consumers stated that a child has been electrocuted. Safety Officer West 1 is requested to visit the subjected site jointly. | N.A. | N.A. | N.A. | N.A. | N.A.
2 | Near H.No E-175, Vishkarma Colony, Lal Kuan, New Delhi | 05.07.2019 at about 12:30 PM | Non-Fatal | A telephonic complaint was received from Lal Kuan near Bharat Gas Godown on 05.07.2019 at about 12:30 PM that a boy named Sanjay aged 8 yrs approximately got electric shock from some nearby cable. Sh. Sahil Lineman and Sh. Surjit Supervisor visited the site and found two incoming cables from pole are cut down and make a temporary arrangement on a wall intentionally for theft purposes by some local public. Also some building works are going on that sitewhere another meter cable also cut down and put U/G from the wall where theft arrangement found. There are no other U/G service line in that area. The boy was playing with his friend near the wall and somehow he touched the open part of the cable and got electric shock. Nearby public / family members taken him to hospital and he is now out of danger. | N.A. | N.A. | N.A. | N.A. | N.A.
3 | j-11 / 135, third floor, Rajouri Garden, New delhi 110027. | 05.07.2019 | Fatal | on dated 05.07.2019 at about 9:50 AM, a PCR Complaint received through online in IOMS vide complaint No 19070502179 regd. Current leakage in house. Immediately Lineman deputed at site who found / informed that an incident of electrocution has been occurred at J-11 / 135 third floor, Rajouri Garden due to current leakage in House electrical wiring. BSES disconnected the power supply of the premise for safety reasons (C.A.No 102889684 & Meter No 40481077) | N.A. | N.A. | N.A. | N.A. | N.A.
4 | Sub Station Bhim Colony, Delhi | 10.07.2019 at about 07:30 PM | Non-Fatal | The information gather from site reveals that a boy of 5 years old named Lucky was playing with his friends near Sub station Bhim Colony, when a ball with which they were playing fell inside the Sub station Bhim Colony. Master Lucky while trying to take out the ball reportedly came in contact with HT 11 kv Line inside Sub station at around 07:30 PM on dated 10.07.2019. In this process, he got an electric shock. The HT line got tripped from the RMU at Priyanka Camp. He was taken to Safdarjung for treatment and is presently under observation in the hospital. | N.A. | N.A. | N.A. | N.A. | N.A.
5 | Jonapur Village, Delhi. | 21.07.2019 | Fatal | The accident took place at connecting road from 7th Avenue RMB to Jonapur Village. There was heavy thunder strom and rain in the Aya Nagar region as per IMD. The BSES HT conductor was broken at 03:35 PM (approximately) and our 11KV O/G feeder NBCC from C DOT grid was tripped / disconnected from NBCC Bhatta Substation, so the reason of accident is not cleared. After accident victims namely Md. Salim and Sh. Hoshiyar Singh Rawat were taken by Delhi Police as per sources. The police has seized the broken conductor. The status quo is as it is from BSES point of view. No BSES employee was present at the time of accident. | N.A. | N.A. | N.A. | N.A. | N.A.
6 | Near Police Station Jaitpur. | 27.07.2019 at about 02:00 AM | Fatal | On 27.07.2019 at about 10:30 AM calls received from public representatives that an electrical accident had occurred on 27.07.2019 at about 02:00 AM when a group of kavadiya boys were moving under 11 kv road crossing conductors of said feeder. The height of the truck along with DJ installations and structures mounted therein was more than specified RTO limits. The probable cause of accident is unknown in which one person is reported to be electrocuted and fell down from the truck - he died. During the night we received individual category NCC at about 02:10 AM and area was checked and when lineman found no fault - the area was energized. Accident situation remained unknown at night. There is regular daily movement of buses and high trucks on this road, but they do not touch the conductors. | N.A. | N.A. | N.A. | N.A. | N.A.
7 | Pole No. BSES SVR V-124 & premise house no. F-33 / 3, GF, Block-F, Gali No. 3, Molarband Extn, Badarpur, New Delhi | 28.07.2019 at about 12:25 PM | Non-Fatal | On dated 28.07.2019 at about 12:25 PM complaint registered for electricity off in the area. Sh. Laki, Lineman visited the site found tripping from sub station no. 8 MB Extn. Also DD fuse blown off at F Block HVDS DP supply restored and at that place found electrical accident occured at Gali No. 3 F Block MB Extn. due to which tripping occured from these places. As per information gathered at site Smt. Punita Kumari victim fell down sariya from roof which was got unballanced and got touched upon the HVDS DD fuse and tripping occured. | N.A. | N.A. | N.A. | N.A. | N.A.

## FORMAT III
FORMAT III: Action taken report for safety measures complied for the accidents occurred
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | Within Specified Time | Beyond specified time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9
Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | 0 | - | 132759 | 132759 | 132759 | 0 | 132759 | 0
Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | 0 | 0 | 23982 | 23982 | 23902 | 80 | 23982 | 0
Continuous power supply failure requiring replacement of distribution transformer. | 0 | 0 | 10 | 10 | 10 | 0 | 10 | 0
Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) | 0 | 0 | 50379 | 50379 | 50379 | 0 | 50379 | 0
Continuous Schduled Power Outage | 0 | 0 | 783 | 783 | 783 | 0 | 783 | 0
Replacement of Burnt Meter or Stolen Meter | 0 | 21 | 4654 | 4675 | 4155 | 491 | 4646 | 29

## FORMAT IV
FORMAT IV: Quality of Power Supply
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | Within Specified Time | Beyond specified time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Local Problem | 4 hours | 0 | 5338 | 5338 | 5338 | 0 | 5338 | 0
Tap setting of transformer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair of Distribution Line/transformer/ capacitor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installation and Up gradation of High Tension/ Low Tension System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT V
FORMAT V: Complaint about meters
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaint lodged for accuracy test of meter-Fast | Within fifteen days | 1200 | 3980 | 5180 | 2526 | 325 | 2851 | 2329
Complaint lodged for accuracy test of meter-Slow | Within fifteen days | 0 | 0 | 0 | 0 | 0 | 0 | 0
Complaint lodged for defective / stuck meter | Within fifteen days | 583 | 2460 | 3043 | 1558 | 1067 | 2625 | 418
Complaint lodged for burnt meter | Restoration of supply with 3hrs and meter to be replaced within 3days. | 962 | 4958 | 5920 | 3516 | 1701 | 5217 | 703
Complaint lodged for stolen meter |  | 5 | 54 | 59 | 41 | 9 | 50 | 9

## FORMAT VI
FORMAT VI: New Connections / Additional Load, where power suppply can be provided from existing network
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
New Connection where no RoW or road Cutting permission is required | 7 days | 4676 | 18621 | 23297 | 11674 | 3996 | 15670 | 7627
New Connection where RoW or road Cutting permission is required | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connection where no RoW or road Cutting permission is required | 7 days | 209 | 223 | 432 | 176 | 27 | 203 | 229
New Connection where RoW or road Cutting permission is required | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT VII
FORMAT VII: Applications for New Connections / Additional Load, where power supply requires extension of distribution system.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
1. Electrified Areas (where extension of line upto five poles is required) | 15 days from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Electrified areas (where extension of lines or augmentation of Distribution Transformer capacity where peak load of transformer has reached 90% of its rated capacity. | Within 2 months from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
3. Electrified areas (where new distribtion transformer is required) | Within 4 months from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
4. Electrified Areas (where existing 11 KV network needs to be augmented) | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Electrified Areas (where existing 66/33 kV substation needs to be augmented) | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connections |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Load |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT VIII
FORMAT VIII: Connection in un-electrified areas
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Un-Electrified Areas (Where connection from nearby existing network is possible) | Within 4 months from Commission's approval | 8 | 11 | 19 | 12 | 0 | 12 | 7
Un-Electrified Areas/ Green Field Projects (Where new network is to be laid or grid station needs to be established) | Within 12 months from Commission's approval | 0 | 1 | 1 | 1 | 0 | 1 | 0

## FORMAT IX
FORMAT IX: Transfer of Consumer's connection and conversion of services.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Transfer of Name | Within two billing cycles of acceptance of application or clearing of dues whichever is later | 187 | 3805 | 3992 | 3762 | 77 | 3839 | 153
Load Reduction | Within ten days of acceptance of application, shall be effective from next billing cycle | 160 | 2551 | 2711 | 2495 | 26 | 2521 | 190
Change of Category | As per Regulation 17 (5) | 848 | 1304 | 2152 | 868 | 57 | 925 | 1227
Incase connection is denied after receipt of payment against demand note | - | 14 | 318 | 332 | 26 | 246 | 272 | 60
Connection energized through Loop | As per Regulation 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If notice towards downward if any is not sent | 31st May of Financial year | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT X
FORMAT X: Complaints about consumer's bills, disconnection, reconnection of supply.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaints on billing | Only one bill in a Financial Year | 1331 | 1255 | 2586 | 1090 | 42 | 1132 | 1454
Final bill for vacation of premises / change of occupance. | 5 days | 49 | 128 | 177 | 130 | 2 | 132 | 45
Non payment of dues by the consumer | 15 days | 10 | 187 | 197 | 186 | 0 | 186 | 11
Request for reconnection | 24hrs | 80 | 1067 | 1147 | 740 | 300 | 1040 | 107
Consumer wanting disconnection | 5 days | 887 | 4927 | 5814 | 3051 | 1963 | 5014 | 800

## FORMAT XI
FORMAT XI: Failure of Distribution Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
No. of Distribution transformers at the beginning of the month |  | No. of Distribution transformers added during the month | Total number of distribution transformers | Failed transformer | % Failure rate of distribution transformers
1 |  | 2 | 3=1+2 | 4 | 5=(4)*100/(3)%
7298 |  | 20 | 7318 | 6 | 8.199%
0 |  | 0 | 0 | 0 | 0
0 |  | 0 | 0 | 0 | 0
0 |  | 0 | 0 | 0 | 0
Note: | Only 3 phase transformers considered>=400 kVA
Only New transformers added in the system is considered against point no. 2
Only O&M failure considered

## FORMAT XII
FORMAT XI: Failure of Power Transformer
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
No. of power transformers at the beginning of the month | No. of power transformers added during the month | Total number of power transformers | Number of power transformers failed | % Failure rate of power transformers
1 | 2 | 3=1+2 | 4 | 5=(4)*100/(3)%
255 | 1 | 256 | 0 | 0%
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0

## FORMAT XIII
FORMAT XIII: Summary of Overall Standards of Performance.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Sl. No. | Service area |  | Overall Standards of Performance | Total Cases Received / Reported (A) | Complaints Attended (B) |  | Standard of Performance Achieved (C)
[5 empty] | Within Specified Time | Beyond specified time
1. Power Supply Failure
(i) | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  | 132759 | 132759 | 0 | 100%
(ii) | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  | 23982 | 23902 | 80 | 99.67%
(iii) | Continuous power supply failure requiring replacement of distribution transformer. | Continuous power supply failure requiring replacement of distribution transformer. |  | 10 | 10 | 0 | 100%
(iv) | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above |  | 50379 | 50379 | 0 | 100%
(v) | Continuous scheduled power outages | Continuous scheduled power outages |  | 783 | 783 | 0 | 100%
(vi) | Replacement of burnt meter | Replacement of burnt meter or stolen meter |  | 4675 | 4155 | 491 | 88.88%
Period of Scheduled Outage
2 | Maximum duration in a single stretch |  |  | 07H:12M | 0 | 0 | 0%
| Restoration of supply by 6:00 PM |  |  | ALL | 0 | 0 | 0%
3 | Faults in street light maintained by the licensee |  |  | 4735 | 4733 | 2 | 99.96%
Reliability Indices
4 | SAIFI |  |  | 0.49 | 0 | 0 | 0
| SAIDI |  |  | 0.28 | 0 | 0 | 0
| CAIDI |  |  | 0.57143 | 0 | 0 | 0
5 | Frequency variation |  |  | 0 | 0 | 0 | 0
6 | Voltage imbalance |  |  | 0 | 0 | 0 | 0
7 | Percentage billing mistakes |  |  | 0 | 0 | 0 | 0

## FORMAT XIV
FORMAT XIV: Compensation Details
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2019-07-01
Year: |  | 2019
Sl. No. | Event |  | Compensation specified for violation of standard |  | Claimed |  | Payable/Paid
[5 empty] | No. of Cases | Amount Claimed | No. of cases in which compensation is payable | Amount of compensation payable in (Rs.) | Amount of compensation paid in (Rs.)
1 | Electricity connections |  |  |  | 0 | 0 | 0 | 0 | 0
(i) | Electrified Areas | Electrified Areas | 1.5% of the demand charges deposited by consumer for each day of default. |  | 0 | 0 | 0 | 0 | 0
(ii) | Augmentation Required | Augmentation Required | 1.5% of the demand charges deposited by consumer for each day of default | 1.5% of the demand charges deposited by consumer for each day of default | 0 | 0 | 0 | 0 | 0
(iii) | Un-electrified Areas | Un-electrified Areas | 1% of the amount deposited by developer/applicants per day of default. | 1% of the amount deposited by developer/applicants per day of default. | 0 | 0 | 0 | 0 | 0
(iv) | Connection denied after receipt of payment against demand note | Connection denied after receipt of payment against demand note | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 0 | 0 | 0 | 0 | 0
(v) | Connection energized through loop | Connection energized through loop | Rs. 500 per kW of sanctioned/ contract demand | Rs. 500 per kW of sanctioned/ contract demand | 0 | 0 | 0 | 0 | 0
2 | Transfer of Name | Transfer of Name | Rs. 100 for each day of default. | Rs. 100 for each day of default. | 0 | 0 | 0 | 0 | 0
3 | Load Reduction | Load Reduction | Rs. 100 for each day of default | Rs. 100 for each day of default | 0 | 0 | 0 | 0 | 0
4 | Notice for downward revision of load | Notice for downward revision of load | Rs. 500 for each case | Rs. 500 for each case | 0 | 0 | 0 | 0 | 0
5 | Change of category | Change of category | Rs. 100 for each day of default | Rs. 100 for each day of default | 0 | 0 | 0 | 0 | 0
6 | Complaints in billing | Complaints in billing | 10% of excess amount billed | 10% of excess amount billed | 0 | 0 | 0 | 0 | 0
7 | Replacement of meters | Replacement of meters | Rs.50 for each day of default | Rs.50 for each day of default | 0 | 0 | 0 | 0 | 0
8 | Fault in street light maintained by the Licensee | Fault in street light maintained by the Licensee | Rs. 75 for each day of default | Rs. 75 for each day of default | 0 | 0 | 0 | 0 | 0
9 | Voltage fluctuations and complainsts | Voltage fluctuations and complainsts |  |  | 0 | 0 | 0 | 0 | 0
10 | Power Supply Failure | Power Supply Failure |  |  | 0 | 0 | 0 | 0 | 0
11 | Total | Total |  |  | 0 | 0 | 0 | 0 | 0

## FORMAT XV
FORMAT XV: Unauthorized Use of Electricity
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
No. of Cases Booked | No. of Cases where UUE is established by the Licensee | No. of cases where appeal filed by the consumer before the Appellate Authority | No. of cases decided by the Appellate Authority in favor of the Licensee | No. of cases decided by the Appellate Authority in the favor of the consumer
747 | 743 | 0 | 3 | 0
0 | 0 | 0 | 0 | 0

## FORMAT XVI
FORMAT XVI: Theft of Electricity
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2019-07-01
Year: | 2019
No. of Cases Booked | No. of complaints filed by the Licensee in Police Station | No. of cases in which judgement delivered by the Special Court | No. of cases decided by the Special Court in favor of Licensee | No. of cases decided by the Special Court in favor of Consumer
1021 | 405 | 4 | 0 | 4
0 | 0 | 0 | 0 | 0