## Sheet1
FORMAT I: Fatal and non-fatal accident report
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Number of Accidents during the month |  |  |  |  | Cumulative since starting of year |  | Cumulative since starting of year
Departmental |  | Outside |  |  | Departmental |  | Outside
FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
2 | 0 | 0 | 0 | 1 | 3 | 3 | 5 | 1 | 4
FH- Fatal Human
NFH- Non Fatal Human
FA- Fatal Animal
FORMAT II: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Sl. No. | Location of accident and details of victim | Date of occurrence | Type of accident | Cause of accident | Findings of CEI/EI /AEI | Remedies suggested by CEI/EI/AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such accidents | Amount paid as compensation
1 | 11 KV NW Indoor Substation in Sub-Division Mukherjee Park, New Delhi. | 01.08.2021 at 11:55 AM | Fatal | While attending the breakdown in the area RG Block, Raghubir Nagar in A-Block Tagore Garden Sub-Division on 01.08.2021 at about 9:08 AM B/D team found that the cable between NW Block, Vishnu Garden to NW Block Kiosk substation was faulty and 3 Panel Board (ABB Make) RMU is moisturized. BD Team isolated the 3 Panel Board by disconnecting all the cables from panel end. The other four Panel Board is charged. B/D team comprising Mr. Jaikishan AMC Supervisor, Mr. Ramavtar L/M, Mr. Pintu L/M, Mr. Hans Raj ALM, and Mr. Sukhvir ALM (M/S Guru Nanak Electricals) AMC Supervisor. Sh. Jaikishan to restore 990 KVA DT, a loop cable from 630 KVA DT to 990 KVA DT was laid with the intent of restoring the power supply. While doing so, lineman did not disconnect the cable from 990 KVA DT, whereas he connected the loop cable, as soon as the power supply was restored the cable between 990 KVA DT and three Panel Board back charged. Thereafter, Mr. Pintu Jha who connected the cable on 990 KVA DT came to panel side to de-moisturize the panel with hot air blower came in contact with the live cable end and got electrocuted. On the same time 11 KV NW Block, Vishnu Garden Feeder tripped from GGSH Grid. The other companions took him to Guru Gobind Singh Hospital, but, he was declared brought dead | N.A. | N.A. | N.A. | N.A. | N.A.
2 | HVDS Pole No. - 4077, Opposite House No. E-30, E-Blk Shiv Enclave, Najafgarg, New Delhi. | 10.08.2021 at 9:15 AM | Fatal | As reported by field staff, Sh. Gourav, lineman was deputed along with Lineman, Sh. Sachin for attending No Current Complaint on 10.08.2021 in Shiv Enclave, E-Block, Najafgarh. The lineman Sh. Gourav disconnected the supply from RMU and asked the ALM to sit there till he comes back. After few minutes the ALM Sh. Sachin was informed by a resident that the lineman has fallen down from pole which caused fatal accident (Report of Post-Mortem is awaited). It was negligence on the part of lineman that no safety equipment was used while attending the complaint. Intimation was given to the police by colony residents and meanwhile, Sh. Sachin immediately informed the SDO and others and arranged to take the victim to Rosewood Hospital, Najafgarh, from where he was referred to Rao Tula Ram Hospital, Jaffarpur, New Delhi. | N.A. | N.A. | N.A. | N.A. | N.A.
3 | Plot No. 5, 6 & 7, Kh. No. 27 / 9 & 10, Ganga Ram Enclave, Kamruddin Nagar, Najafgarh Road, Kanwar Singh Nagar, Nangloi, Near Hanuman Mandir, New Delhi. | 17.08.2021 at about 7:17 Hrs. | Non-Fatal | It has been reported by Sh. C. L. Saraswat, AsVP EHV TRL West that they learnt about this accident on 20.08.2021 from one of leading newspaper. As learnt from newspaper, the victim climbed upon the roof of the godown / factory for collecting some material where he accidently touched the passing 66 KV High Tension line. As learnt from newspaper, the victim was immediately taken to hospital for primary care and after that he was referred to Safdarjung Hospital. After getting the information from newspaper, we visited the site and enquired about the accident. We immediately informed to Asstt. Electrical Inspector and Electrical Inspector about the accident. We visited the site the same day, but, the premise was found locked. | N.A. | N.A. | N.A. | N.A. | N.A.
FORMAT III: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | Within Specified Time | Beyond specified time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9
Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  |  | - | 35349 | 35349 | 35349 | 0 | 35349 | 0
Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  |  |  | 2997 | 2997 | 2997 | 0 | 2997 | 0
Continuous power supply failure requiring replacement of distribution transformer. |  |  |  | 6 | 6 | 5 | 1 | 6 | 0
Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) |  |  |  | 13340 | 13340 | 13340 | 0 | 13340 | 0
Continuous Schduled Power Outage |  |  |  | 445 | 445 | 445 | 0 | 445 | 0
Replacement of Burnt Meter or Stolen Meter |  |  | 315 | 3892 | 4207 | 3291 | 552 | 3843 | 364
FORMAT IV: Quality of Power Supply
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | Within Specified Time | Beyond specified time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Local Problem |  | 4 hours | 0 | 1129 | 1129 | 1129 | 0 | 1129 | 0
Tap setting of transformer
Repair of Distribution Line/transformer/ capacitor
Installation and Up gradation of High Tension/ Low Tension System
FORMAT V: Complaint about meters
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaint lodged for accuracy test of meter-Fast |  | Within fifteen days | 1881 | 5349 | 7230 | 3464 | 542 | 4006 | 3224
Complaint lodged for accuracy test of meter-Slow |  | Within fifteen days | 0 | 0 | 0 | 0 | 0 | 0 | 0
Complaint lodged for defective / stuck meter |  | Within fifteen days | 473 | 1996 | 2469 | 1183 | 784 | 1967 | 502
Complaint lodged for burnt meter |  | Restoration of supply with 3hrs and meter to be replaced within 3days. | 906 | 4006 | 4912 | 2462 | 1735 | 4197 | 715
Complaint lodged for stolen meter |  |  | 14 | 56 | 70 | 36 | 26 | 62 | 8
FORMAT VI: New Connections / Additional Load, where power suppply can be provided from existing network
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
New Connection where no RoW or road Cutting permission is required |  | 7 days | 6435 | 22574 | 29009 | 18655 | 3063 | 21718 | 7291
New Connection where RoW or road Cutting permission is required |  | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connection where no RoW or road Cutting permission is required |  | 7 days | 134 | 492 | 626 | 435 | 21 | 456 | 170
New Connection where RoW or road Cutting permission is required |  | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT VII: Applications for New Connections / Additional Load, where power supply requires extension of distribution system.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
1. Electrified Areas (where extension of line upto five poles is required) |  | 15 days from receipt of payment
2. Electrified areas (where extension of lines or augmentation of Distribution Transformer capacity where peak load of transformer has reached 90% of its rated capacity. |  | Within 2 months from receipt of payment
3. Electrified areas (where new distribtion transformer is required) |  | Within 4 months from receipt of payment
4. Electrified Areas (where existing 11 KV network needs to be augmented) |  | 15 days
5. Electrified Areas (where existing 66/33 kV substation needs to be augmented) |  | 15 days
New Connections |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Load |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT VIII: Connection in un-electrified areas
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Un-Electrified Areas (Where connection from nearby existing network is possible) |  | Within 4 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0
Un-Electrified Areas/ Green Field Projects (Where new network is to be laid or grid station needs to be established) |  | Within 12 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT IX: Transfer of Consumer's connection and conversion of services.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Transfer of Name |  | Within two billing cycles of acceptance of application or clearing of dues whichever is later | 368 | 2882 | 3250 | 2798 | 168 | 2966 | 284
Load Reduction |  | Within ten days of acceptance of application, shall be effective from next billing cycle | 177 | 1429 | 1606 | 1378 | 88 | 1466 | 140
Change of Category |  | As per Regulation 17 (5) | 307 | 510 | 817 | 424 | 55 | 479 | 338
Incase connection is denied after receipt of payment against demand note |  | - | 155 | 1158 | 1313 | 429 | 884 | 1313 | 0
Connection energized through Loop |  | As per Regulation 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If notice towards downward if any is not sent |  | 31st May of Financial year | 0 | 0 | 0 | 0 | 0 | 0 | 0
FORMAT X: Complaints about consumer's bills, disconnection, reconnection of supply.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Service Area |  | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[6 empty] | With in Specified Time | Beyond Specified Time | Total
1 |  | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaints on billing |  | Only one bill in a Financial Year | 851 | 1461 | 2312 | 1162 | 427 | 1589 | 723
Final bill for vacation of premises / change of occupance. |  | 5 days | 340 | 523 | 863 | 484 | 273 | 757 | 106
Non payment of dues by the consumer |  | 15 days | 33 | 87 | 120 | 93 | 3 | 96 | 24
Request for reconnection |  | 24hrs | 89 | 721 | 810 | 538 | 180 | 718 | 92
Consumer wanting disconnection |  | 5 days | 1086 | 5122 | 6208 | 3285 | 2008 | 5293 | 915
FORMAT XI: Failure of Distribution Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
No. of Distribution transformers at the beginning of the month |  | No. of Distribution transformers added during the month |  | Total number of distribution transformers |  | Number of Distribution transformers failed |  | % Failure rate of distribution transformers
1 |  | 2 |  | 3=1+2 |  | 4 |  | 5=(4)*100/(3)%
7724 |  | 6 |  | 7730 |  | 3 |  | 3.881%
Note: | Only 3 phase transformers considered>=400 kVA
Only New transformers added in the system is considered against point no. 2
Only O&M failure considered
FORMAT XII: Failure of Power Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
No. of power transformers at the beginning of the month |  | No. of power transformers added during the month |  | Total number of power transformers |  | Number of power transformers failed |  | % Failure rate of power transformers
1 |  | 2 |  | 3=1+2 |  | 4 |  | 5=(4)*100/(3)%
265 |  | 0 |  | 265 |  | 0 |  | 0%
FORMAT XIII: Summary of Overall Standards of Performance.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Sl. No. | Service area |  | Overall Standards of Performance | Total Cases Received / Reported (A) |  | Complaints Attended (B) |  | Standard of Performance Achieved (C)
[6 empty] | Within Specified Time | Beyond specified time
1. Power Supply Failure
(i) | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  | 35349 |  | 35349 | 0 | 100%
(ii) | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  | 2997 |  | 2997 | 0 | 100%
(iii) | Continuous power supply failure requiring replacement of distribution transformer. | Continuous power supply failure requiring replacement of distribution transformer. |  | 6 |  | 5 | 1 | 83.33%
(iv) | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above |  | 13340 |  | 13340 | 0 | 100%
(v) | Continuous scheduled power outages | Continuous scheduled power outages |  | 445 |  | 445 | 0 | 100%
(vi) | Replacement of burnt meter | Replacement of burnt meter or stolen meter |  | 4270 |  | 3291 | 552 | 78.23%
Period of Scheduled Outage
2 | Maximum duration in a single stretch |  |  | 6H:32M
| Restoration of supply by 6:00 PM |  |  | ALL
3 | Faults in street light maintained by the licensee |  |  | 2353 |  | 2353 | 0 | 100%
Reliability Indices
4 | SAIFI |  |  | 0.38
| SAIDI |  |  | 0.21
| CAIDI |  |  | 0.55263
5 | Frequency variation |  |  | 0 |  | 0 | 0 | 0
6 | Voltage imbalance |  |  | 0 |  | 0 | 0 | 0
7 | Percentage billing mistakes |  |  | 0 |  | 0 | 0 | 0
* New method used for reliabilty index calculation*
FORMAT XIV: Compensation Details
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Sl. No. | Event |  | Compensation specified for violation of standard |  | Claimed |  | Payable/Paid
[5 empty] | No. of Cases | Amount Claimed | No. of cases in which compensation is payable | Amount of compensation payable in (Rs.) | Amount of compensation paid in (Rs.)
1 | Electricity connections
(i) | Electrified Areas | Electrified Areas | 1.5% of the demand charges deposited by consumer for each day of default.
(ii) | Augmentation Required | Augmentation Required | 1.5% of the demand charges deposited by consumer for each day of default | 1.5% of the demand charges deposited by consumer for each day of default
(iii) | Un-electrified Areas | Un-electrified Areas | 1% of the amount deposited by developer/applicants per day of default. | 1% of the amount deposited by developer/applicants per day of default.
(iv) | Connection denied after receipt of payment against demand note | Connection denied after receipt of payment against demand note | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment.
(v) | Connection energized through loop | Connection energized through loop | Rs. 500 per kW of sanctioned/ contract demand | Rs. 500 per kW of sanctioned/ contract demand
2 | Transfer of Name | Transfer of Name | Rs. 100 for each day of default. | Rs. 100 for each day of default.
3 | Load Reduction | Load Reduction | Rs. 100 for each day of default | Rs. 100 for each day of default
4 | Notice for downward revision of load | Notice for downward revision of load | Rs. 500 for each case | Rs. 500 for each case
5 | Change of category | Change of category | Rs. 100 for each day of default | Rs. 100 for each day of default
6 | Complaints in billing | Complaints in billing | 10% of excess amount billed | 10% of excess amount billed
7 | Replacement of meters | Replacement of meters | Rs.50 for each day of default | Rs.50 for each day of default
8 | Fault in street light maintained by the Licensee | Fault in street light maintained by the Licensee | Rs. 75 for each day of default | Rs. 75 for each day of default
9 | Voltage fluctuations and complainsts | Voltage fluctuations and complainsts
10 | Power Supply Failure | Power Supply Failure
11 | Total | Total
FORMAT XV: Unauthorized Use of Electricity
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
No. of Cases Booked |  | No. of Cases where UUE is established by the Licensee |  | No. of cases where appeal filed by the consumer before the Appellate Authority |  | No. of cases decided by the Appellate Authority in favor of the Licensee |  | No. of cases decided by the Appellate Authority in the favor of the consumer
93 |  | 63 |  | 0 |  | 2 |  | 0
FORMAT XVI: Theft of Electricity
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
No. of Cases Booked |  | No. of complaints filed by the Licensee in Police Station |  | No. of cases in which judgement delivered by the Special Court |  | No. of cases decided by the Special Court in favor of Licensee |  | No. of cases decided by the Special Court in favor of Consumer
3195 |  | 881 |  | 0 |  | 0 |  | 0

## FORMAT I
FORMAT I: Fatal and non-fatal accident report
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Number of Accidents during the month |  |  |  |  | Cumulative since starting of year |  | Cumulative since starting of year
Departmental |  | Outside |  |  | Departmental |  | Outside
FH | NFH | FH | FA | NFH | FH | NFH | FH | FA | NFH
2 | 0 | 0 | 0 | 1 | 3 | 3 | 5 | 1 | 4
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FH- Fatal Human
NFH- Non Fatal Human
FA- Fatal Animal

## FORMAT II
FORMAT II: Action taken report for safety measures complied for the accidents occurred
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Sl. No. | Location of accident and details of victim | Date of occurrence | Type of accident | Cause of accident | Findings of CEI/EI /AEI | Remedies suggested by CEI/EI/AEI in various cases | Whether the remedy suggested is complied | Action taken to avoid recurrence of such accidents | Amount paid as compensation
1 | 11 KV NW Indoor Substation in Sub-Division Mukherjee Park, New Delhi. | 01.08.2021 at 11:55 AM | Fatal | While attending the breakdown in the area RG Block, Raghubir Nagar in A-Block Tagore Garden Sub-Division on 01.08.2021 at about 9:08 AM B/D team found that the cable between NW Block, Vishnu Garden to NW Block Kiosk substation was faulty and 3 Panel Board (ABB Make) RMU is moisturized. BD Team isolated the 3 Panel Board by disconnecting all the cables from panel end. The other four Panel Board is charged. B/D team comprising Mr. Jaikishan AMC Supervisor, Mr. Ramavtar L/M, Mr. Pintu L/M, Mr. Hans Raj ALM, and Mr. Sukhvir ALM (M/S Guru Nanak Electricals) AMC Supervisor. Sh. Jaikishan to restore 990 KVA DT, a loop cable from 630 KVA DT to 990 KVA DT was laid with the intent of restoring the power supply. While doing so, lineman did not disconnect the cable from 990 KVA DT, whereas he connected the loop cable, as soon as the power supply was restored the cable between 990 KVA DT and three Panel Board back charged. Thereafter, Mr. Pintu Jha who connected the cable on 990 KVA DT came to panel side to de-moisturize the panel with hot air blower came in contact with the live cable end and got electrocuted. On the same time 11 KV NW Block, Vishnu Garden Feeder tripped from GGSH Grid. The other companions took him to Guru Gobind Singh Hospital, but, he was declared brought dead | N.A. | N.A. | N.A. | N.A. | N.A.
2 | HVDS Pole No. - 4077, Opposite House No. E-30, E-Blk Shiv Enclave, Najafgarg, New Delhi. | 10.08.2021 at 9:15 AM | Fatal | As reported by field staff, Sh. Gourav, lineman was deputed along with Lineman, Sh. Sachin for attending No Current Complaint on 10.08.2021 in Shiv Enclave, E-Block, Najafgarh. The lineman Sh. Gourav disconnected the supply from RMU and asked the ALM to sit there till he comes back. After few minutes the ALM Sh. Sachin was informed by a resident that the lineman has fallen down from pole which caused fatal accident (Report of Post-Mortem is awaited). It was negligence on the part of lineman that no safety equipment was used while attending the complaint. Intimation was given to the police by colony residents and meanwhile, Sh. Sachin immediately informed the SDO and others and arranged to take the victim to Rosewood Hospital, Najafgarh, from where he was referred to Rao Tula Ram Hospital, Jaffarpur, New Delhi. | N.A. | N.A. | N.A. | N.A. | N.A.
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Plot No. 5, 6 & 7, Kh. No. 27 / 9 & 10, Ganga Ram Enclave, Kamruddin Nagar, Najafgarh Road, Kanwar Singh Nagar, Nangloi, Near Hanuman Mandir, New Delhi. | 17.08.2021 at about 7:17 Hrs. | Non-Fatal | It has been reported by Sh. C. L. Saraswat, AsVP EHV TRL West that they learnt about this accident on 20.08.2021 from one of leading newspaper. As learnt from newspaper, the victim climbed upon the roof of the godown / factory for collecting some material where he accidently touched the passing 66 KV High Tension line. As learnt from newspaper, the victim was immediately taken to hospital for primary care and after that he was referred to Safdarjung Hospital. After getting the information from newspaper, we visited the site and enquired about the accident. We immediately informed to Asstt. Electrical Inspector and Electrical Inspector about the accident. We visited the site the same day, but, the premise was found locked. | N.A. | N.A. | N.A. | N.A. | N.A.

## FORMAT III
FORMAT III: Action taken report for safety measures complied for the accidents occurred
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | Within Specified Time | Beyond specified time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9
Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | 0 | - | 35349 | 35349 | 35349 | 0 | 35349 | 0
Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | 0 | 0 | 2997 | 2997 | 2997 | 0 | 2997 | 0
Continuous power supply failure requiring replacement of distribution transformer. | 0 | 0 | 6 | 6 | 5 | 1 | 6 | 0
Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) | 0 | 0 | 13340 | 13340 | 13340 | 0 | 13340 | 0
Continuous Schduled Power Outage | 0 | 0 | 445 | 445 | 445 | 0 | 445 | 0
Replacement of Burnt Meter or Stolen Meter | 0 | 315 | 3892 | 4207 | 3291 | 552 | 3843 | 364

## FORMAT IV
FORMAT IV: Quality of Power Supply
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | Within Specified Time | Beyond specified time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Local Problem | 4 hours | 0 | 1129 | 1129 | 1129 | 0 | 1129 | 0
Tap setting of transformer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair of Distribution Line/transformer/ capacitor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Installation and Up gradation of High Tension/ Low Tension System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT V
FORMAT V: Complaint about meters
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaint lodged for accuracy test of meter-Fast | Within fifteen days | 1881 | 5349 | 7230 | 3464 | 542 | 4006 | 3224
Complaint lodged for accuracy test of meter-Slow | Within fifteen days | 0 | 0 | 0 | 0 | 0 | 0 | 0
Complaint lodged for defective / stuck meter | Within fifteen days | 473 | 1996 | 2469 | 1183 | 784 | 1967 | 502
Complaint lodged for burnt meter | Restoration of supply with 3hrs and meter to be replaced within 3days. | 906 | 4006 | 4912 | 2462 | 1735 | 4197 | 715
Complaint lodged for stolen meter |  | 14 | 56 | 70 | 36 | 26 | 62 | 8

## FORMAT VI
FORMAT VI: New Connections / Additional Load, where power suppply can be provided from existing network
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
New Connection where no RoW or road Cutting permission is required | 7 days | 6435 | 22574 | 29009 | 18655 | 3063 | 21718 | 7291
New Connection where RoW or road Cutting permission is required | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connection where no RoW or road Cutting permission is required | 7 days | 134 | 492 | 626 | 435 | 21 | 456 | 170
New Connection where RoW or road Cutting permission is required | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT VII
FORMAT VII: Applications for New Connections / Additional Load, where power supply requires extension of distribution system.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
1. Electrified Areas (where extension of line upto five poles is required) | 15 days from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
2. Electrified areas (where extension of lines or augmentation of Distribution Transformer capacity where peak load of transformer has reached 90% of its rated capacity. | Within 2 months from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
3. Electrified areas (where new distribtion transformer is required) | Within 4 months from receipt of payment | 0 | 0 | 0 | 0 | 0 | 0 | 0
4. Electrified Areas (where existing 11 KV network needs to be augmented) | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
5. Electrified Areas (where existing 66/33 kV substation needs to be augmented) | 15 days | 0 | 0 | 0 | 0 | 0 | 0 | 0
New Connections |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Load |  | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT VIII
FORMAT VIII: Connection in un-electrified areas
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Un-Electrified Areas (Where connection from nearby existing network is possible) | Within 4 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0
Un-Electrified Areas/ Green Field Projects (Where new network is to be laid or grid station needs to be established) | Within 12 months from Commission's approval | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT IX
FORMAT IX: Transfer of Consumer's connection and conversion of services.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Transfer of Name | Within two billing cycles of acceptance of application or clearing of dues whichever is later | 368 | 2882 | 3250 | 2798 | 168 | 2966 | 284
Load Reduction | Within ten days of acceptance of application, shall be effective from next billing cycle | 177 | 1429 | 1606 | 1378 | 88 | 1466 | 140
Change of Category | As per Regulation 17 (5) | 307 | 510 | 817 | 424 | 55 | 479 | 338
Incase connection is denied after receipt of payment against demand note | - | 155 | 1158 | 1313 | 429 | 884 | 1313 | 0
Connection energized through Loop | As per Regulation 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
If notice towards downward if any is not sent | 31st May of Financial year | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FORMAT X
FORMAT X: Complaints about consumer's bills, disconnection, reconnection of supply.
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
Service Area | Standard | Pending complaint of the previous month | Complaint received during the month | Total Complaint | Complaints attended during the month |  |  | Balance complaint to be attended
[5 empty] | With in Specified Time | Beyond Specified Time | Total
1 | 2 | 3 | 4 | 5=3+4 | 6 | 7 | 8=6+7 | 9=5-8
Complaints on billing | Only one bill in a Financial Year | 851 | 1461 | 2312 | 1162 | 427 | 1589 | 723
Final bill for vacation of premises / change of occupance. | 5 days | 340 | 523 | 863 | 484 | 273 | 757 | 106
Non payment of dues by the consumer | 15 days | 33 | 87 | 120 | 93 | 3 | 96 | 24
Request for reconnection | 24hrs | 89 | 721 | 810 | 538 | 180 | 718 | 92
Consumer wanting disconnection | 5 days | 1086 | 5122 | 6208 | 3285 | 2008 | 5293 | 915

## FORMAT XI
FORMAT XI: Failure of Distribution Transformer
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
No. of Distribution transformers at the beginning of the month |  | No. of Distribution transformers added during the month | Total number of distribution transformers | Failed transformer | % Failure rate of distribution transformers
1 |  | 2 | 3=1+2 | 4 | 5=(4)*100/(3)%
7724 |  | 6 | 7730 | 3 | 3.881%
0 |  | 0 | 0 | 0 | 0
0 |  | 0 | 0 | 0 | 0
0 |  | 0 | 0 | 0 | 0
Note: | Only 3 phase transformers considered>=400 kVA
Only New transformers added in the system is considered against point no. 2
Only O&M failure considered

## FORMAT XII
FORMAT XI: Failure of Power Transformer
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
No. of power transformers at the beginning of the month | No. of power transformers added during the month | Total number of power transformers | Number of power transformers failed | % Failure rate of power transformers
1 | 2 | 3=1+2 | 4 | 5=(4)*100/(3)%
265 | 0 | 265 | 0 | 0%
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0

## FORMAT XIII
FORMAT XIII: Summary of Overall Standards of Performance.
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Sl. No. | Service area |  | Overall Standards of Performance | Total Cases Received / Reported (A) | Complaints Attended (B) |  | Standard of Performance Achieved (C)
[5 empty] | Within Specified Time | Beyond specified time
1. Power Supply Failure
(i) | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting individual consumer and group of consumer upto 100 connected at Low voltage supply, excluding the failure where distribution transformer requires replacement. |  | 35349 | 35349 | 0 | 100%
(ii) | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. | Continuous power failure affecting more than 100 consumers connected at Low voltage supply excluding the failure where distribution transformer requires replacement. |  | 2997 | 2997 | 0 | 100%
(iii) | Continuous power supply failure requiring replacement of distribution transformer. | Continuous power supply failure requiring replacement of distribution transformer. |  | 6 | 5 | 1 | 83.33%
(iv) | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above | Continuous power failure affecting consumers connected through High Voltage Distribution System (HVDS) and not covered under (i) & (ii) above |  | 13340 | 13340 | 0 | 100%
(v) | Continuous scheduled power outages | Continuous scheduled power outages |  | 445 | 445 | 0 | 100%
(vi) | Replacement of burnt meter | Replacement of burnt meter or stolen meter |  | 4270 | 3291 | 552 | 78.23%
Period of Scheduled Outage
2 | Maximum duration in a single stretch |  |  | 6H:32M | 0 | 0 | 0%
| Restoration of supply by 6:00 PM |  |  | ALL | 0 | 0 | 0%
3 | Faults in street light maintained by the licensee |  |  | 2353 | 2353 | 0 | 100%
Reliability Indices
4 | SAIFI |  |  | 0.38 | 0 | 0 | 0
| SAIDI |  |  | 0.21 | 0 | 0 | 0
| CAIDI |  |  | 0.55263 | 0 | 0 | 0
5 | Frequency variation |  |  | 0 | 0 | 0 | 0
6 | Voltage imbalance |  |  | 0 | 0 | 0 | 0
7 | Percentage billing mistakes |  |  | 0 | 0 | 0 | 0

## FORMAT XIV
FORMAT XIV: Compensation Details
Name of Company: |  | BSES RAJDHANI POWER LIMITED.
Period of Report: |  | 2021-08-01
Year: |  | 2021
Sl. No. | Event |  | Compensation specified for violation of standard |  | Claimed |  | Payable/Paid
[5 empty] | No. of Cases | Amount Claimed | No. of cases in which compensation is payable | Amount of compensation payable in (Rs.) | Amount of compensation paid in (Rs.)
1 | Electricity connections |  |  |  | 0 | 0 | 0 | 0 | 0
(i) | Electrified Areas | Electrified Areas | 1.5% of the demand charges deposited by consumer for each day of default. |  | 0 | 0 | 0 | 0 | 0
(ii) | Augmentation Required | Augmentation Required | 1.5% of the demand charges deposited by consumer for each day of default | 1.5% of the demand charges deposited by consumer for each day of default | 0 | 0 | 0 | 0 | 0
(iii) | Un-electrified Areas | Un-electrified Areas | 1% of the amount deposited by developer/applicants per day of default. | 1% of the amount deposited by developer/applicants per day of default. | 0 | 0 | 0 | 0 | 0
(iv) | Connection denied after receipt of payment against demand note | Connection denied after receipt of payment against demand note | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 1.5% of the demand charges deposited by consumer for each day of default subject to maximum of the amount paid as per demand note. Default to be computed from the date of receipt of payment. | 0 | 0 | 0 | 0 | 0
(v) | Connection energized through loop | Connection energized through loop | Rs. 500 per kW of sanctioned/ contract demand | Rs. 500 per kW of sanctioned/ contract demand | 0 | 0 | 0 | 0 | 0
2 | Transfer of Name | Transfer of Name | Rs. 100 for each day of default. | Rs. 100 for each day of default. | 0 | 0 | 0 | 0 | 0
3 | Load Reduction | Load Reduction | Rs. 100 for each day of default | Rs. 100 for each day of default | 0 | 0 | 0 | 0 | 0
4 | Notice for downward revision of load | Notice for downward revision of load | Rs. 500 for each case | Rs. 500 for each case | 0 | 0 | 0 | 0 | 0
5 | Change of category | Change of category | Rs. 100 for each day of default | Rs. 100 for each day of default | 0 | 0 | 0 | 0 | 0
6 | Complaints in billing | Complaints in billing | 10% of excess amount billed | 10% of excess amount billed | 0 | 0 | 0 | 0 | 0
7 | Replacement of meters | Replacement of meters | Rs.50 for each day of default | Rs.50 for each day of default | 0 | 0 | 0 | 0 | 0
8 | Fault in street light maintained by the Licensee | Fault in street light maintained by the Licensee | Rs. 75 for each day of default | Rs. 75 for each day of default | 0 | 0 | 0 | 0 | 0
9 | Voltage fluctuations and complainsts | Voltage fluctuations and complainsts |  |  | 0 | 0 | 0 | 0 | 0
10 | Power Supply Failure | Power Supply Failure |  |  | 0 | 0 | 0 | 0 | 0
11 | Total | Total |  |  | 0 | 0 | 0 | 0 | 0

## FORMAT XV
FORMAT XV: Unauthorized Use of Electricity
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
No. of Cases Booked | No. of Cases where UUE is established by the Licensee | No. of cases where appeal filed by the consumer before the Appellate Authority | No. of cases decided by the Appellate Authority in favor of the Licensee | No. of cases decided by the Appellate Authority in the favor of the consumer
93 | 63 | 0 | 2 | 0
0 | 0 | 0 | 0 | 0

## FORMAT XVI
FORMAT XVI: Theft of Electricity
Name of Company: | BSES RAJDHANI POWER LIMITED.
Period of Report: | 2021-08-01
Year: | 2021
No. of Cases Booked | No. of complaints filed by the Licensee in Police Station | No. of cases in which judgement delivered by the Special Court | No. of cases decided by the Special Court in favor of Licensee | No. of cases decided by the Special Court in favor of Consumer
3195 | 881 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0